## Input Parameters
Cooling Tower - Input Parameters
Project: Sample Cooling Tower ¦ Engineer: Engineer ¦ Date: 2026-03-13
Parameter | Value | Unit
Circulation Water Flow (Q) | 500 | m³/h
Inlet Water Temp (T_in) | 37 | °C
Outlet Water Temp (T_out) | 32 | °C
Temperature Difference (ΔT) | 5 | °C
Dry Bulb Temperature (Tdb) | 35 | °C
Wet Bulb Temperature (Twb) | 28 | °C
Air Flow Rate (G) | 400000 | m³/h
Fill Characteristic (KaV/L) | 1.5 | -
Cycles of Concentration (COC) | 3 | -
Tower Type | Counter-flow | -
Season | Summer (C=1.0) | -
Atmospheric Pressure | 101.325 | kPa
Water Density | 1000 | kg/m³
Specific Heat of Water | 4.186 | kJ/(kg·°C)
Air Density (approx.) | 1.2 | kg/m³

## Calculation Steps
Step-by-Step Calculation Process
Step | Formula | Substitution | Result
1. Temperature Difference | ΔT = T_in - T_out | 37 - 32 | 5.0 °C
2. Evaporation Coeff (C) | C = 1.0 (summer) | - | 1.0
3. Simple Evaporation | E = C × ΔT × Q / 600 | 1.0 × 5.0 × 500.0 / 600 | 4.1667 m³/h
4. Water Mass Flow (L) | L = Q × ρw / 3600 | 500.0 × 1000 / 3600 | 138.89 kg/s
5. Air Mass Flow (G_m) | G_m = G × ρa / 3600 | 400000.0 × 1.2 / 3600 | 133.33 kg/s
6. L/G Ratio | L/G = L / G_m | 138.89 / 133.33 | 1.042
7. Merkel Number | NTU = ∫(Cp·dT)/(h_s - h_a) | Numerical integration (Simpson) | 0.394
8. Merkel Evaporation | From enthalpy balance | G_m × ΔW | 7.9460 m³/h
9. Splash Loss Rate | Rate = 0.1% of Q | 0.001 × 500.0 | 0.5000 m³/h
10. Blowdown | BD = E / (COC - 1) | 7.9460 / (3.0 - 1) | 3.9730 m³/h
11. Total Makeup | Total = E + Splash + BD | 7.9460 + 0.5000 + 3.9730 | 12.4190 m³/h
12. Approach Temp | Approach = T_out - T_wb | 32.0 - 5.0 | 5.0 °C
13. Cooling Range | Range = T_in - T_out | 37.0 - 32.0 | 5.0 °C
14. Efficiency | η = Range / (Range + Approach) | 5.0 / (5.0 + 5.0) | 50.0 %

## Results Summary
Results Summary (with Live Formulas)
Editable Inputs
Parameter | Value | Unit
Circulation Flow | 500 | m³/h
Inlet Water Temp | 37 | °C
Outlet Water Temp | 32 | °C
Evaporation Coeff | 1 | -
Cycles of Concentration | 3 | -
Splash Loss Rate | 0.001 | -
Calculated Results (Auto-update)
Item | Formula | Result | Unit
ΔT (Temp Diff) | B6-B7 |  | °C
Simple Evaporation | B8*(B6-B7)*B5/600 |  | m³/h
Splash Loss | B10*B5 |  | m³/h
Blowdown (est.) | B8*(B6-B7)*B5/600/(B9-1) |  | m³/h
Total Makeup (Simple) | B8*(B6-B7)*B5/600+B10*B5+B8*(B6-B7)*B5/600/(B9-1) |  | m³/h
Daily Makeup | (B8*(B6-B7)*B5/600+B10*B5+B8*(B6-B7)*B5/600/(B9-1))*24 |  | m³/day
Monthly Makeup | (B8*(B6-B7)*B5/600+B10*B5+B8*(B6-B7)*B5/600/(B9-1))*24*30 |  | m³/month

## Sensitivity Analysis
Sensitivity Analysis Matrix
Effect of Temperature Difference (ΔT)
ΔT (°C) | E_simple (m³/h) | E_total (m³/h)
2
3
4
5
6
7
8
10
12
15
Effect of Cycles of Concentration (COC)
COC | Blowdown (m³/h) | Total Makeup (m³/h) | Water Saved vs COC=2 (%)
1.5
2
2.5
3
3.5
4
5
6
8
10
Effect of Circulation Flow Rate (Q)
Q (m³/h) | Evaporation (m³/h) | Total Makeup (m³/h)
100
200
300
500
750
1000
1500
2000