Cooling Tower
Evaporation Analysis Report

____________________________________________________________

Project: Sample Cooling Tower

Engineer: Engineer

Date: 2026-03-13

# Table of Contents

1. Input Parameters

2. Calculation Methodology

3. Calculation Results

4. Water Loss Distribution

5. Air Properties

6. Charts and Analysis

7. Conclusions and Recommendations

Appendix A: Formula Reference

# 1. Input Parameters

The following parameters were used for the cooling tower evaporation analysis. All values are based on design conditions or field measurements.

| Parameter | Value | Unit |
| --- | --- | --- |
| Circulation Water Flow (Q) | 500.0 | m³/h |
| Inlet Water Temp (T_in) | 37.0 | °C |
| Outlet Water Temp (T_out) | 32.0 | °C |
| Temperature Difference (ΔT) | 5.0 | °C |
| Dry Bulb Temperature | 35.0 | °C |
| Wet Bulb Temperature | 28.0 | °C |
| Air Flow Rate (G) | 400000.0 | m³/h |
| Fill Characteristic (KaV/L) | 1.50 | - |
| Cycles of Concentration | 3.0 | - |
| Tower Type | Counter-flow | - |
| Season | Summer (C=1.0) | - |

# 2. Calculation Methodology

## 2.1 Simple Empirical Formula

E = C x ΔT x Q / 600

Where E = evaporation rate (m³/h), C = evaporation coefficient (1.0 for summer, 0.8 for winter), ΔT = temperature difference (°C), Q = circulation flow rate (m³/h).

## 2.2 Merkel Enthalpy Difference Method

The Merkel method uses numerical integration of the enthalpy difference between saturated air at the water temperature and the actual air enthalpy. This method accounts for the air-water mass transfer process and provides more accurate results when air flow data is available.

Key parameters include the L/G ratio (liquid-to-gas mass flow ratio), the Merkel number (KaV/L), and the approach temperature.

## 2.3 Water Loss Components

Total makeup water = Evaporation + Splash Loss + Blowdown. Splash loss rate: 0.1% of circulation flow. Blowdown is calculated from COC: Blowdown = Evaporation / (COC - 1).

# 3. Calculation Results

| Item | Value | Unit |
| --- | --- | --- |
| L/G Ratio | 1.042 | - |
| Merkel Number | 0.394 | - |
| Evaporation - Simple | 4.1667 | m³/h |
| Evaporation - Merkel | 7.9460 | m³/h |
| Splash Loss | 0.5000 | m³/h |
| Blowdown Loss | 3.9730 | m³/h |
| Total Makeup Water | 12.4190 | m³/h |
| Cooling Efficiency | 50.0 | % |
| Approach Temperature | 5.0 | °C |
| Cooling Range | 5.0 | °C |

# 4. Water Loss Distribution

| Loss Type | Flow (m³/h) | Percentage (%) |
| --- | --- | --- |
| Evaporation | 7.9460 | 64.0 |
| Splash | 0.5000 | 4.0 |
| Blowdown | 3.9730 | 32.0 |
| Total | 12.4190 | 100.0 |

# 5. Ambient Air Properties

| Property | Inlet | Outlet | Unit |
| --- | --- | --- | --- |
| Temperature | 35.0 | 35.5 | °C |
| Humidity Ratio | 0.02110 | 0.03016 | kg/kg |
| Enthalpy | 89.35 | 113.15 | kJ/kg |
| Relative Humidity | 59.1 | - | % |

# 7. Conclusions and Recommendations

Total makeup water requirement is 12.4190 m³/h, equivalent to approximately 298.1 m³/day or 8942 m³/month.

Cooling efficiency is below 50%. Inspect fill condition, fan performance, and drift eliminators.

# Appendix A: Formula Reference

## A.1 Saturation Vapor Pressure

Ps = 0.61078 x exp(17.27 x T / (T + 237.3))  [kPa]

## A.2 Humidity Ratio

W = 0.622 x Pw / (P - Pw)  [kg water / kg dry air]

## A.3 Moist Air Enthalpy

h = 1.006 x T + W x (2501 + 1.86 x T)  [kJ/kg dry air]

## A.4 Cooling Tower Efficiency

Efficiency = Range / (Range + Approach) x 100%

Range = T_in - T_out ; Approach = T_out - T_wb

## A.5 Assumptions

Atmospheric pressure: 101.325 kPa (sea level)

Water density: 1000 kg/m³

Specific heat of water: 4.186 kJ/(kg·°C)

Air density: 1.2 kg/m³ (approximate)

Steady-state operation assumed